## PV PLANT BoQ
Project | Webinar- Topography
Design | Webinar- Topography-0 | Date | 2024/02/15
Item |  | Unit | Quantity
1 | MAIN EQUIPMENT
1.1 | PV module
1.1.1 | CSI Solar Co., Ltd. - CS7L-610TB-AG 1500V (610 W bifacial Si-mono). Dimensions 2172.0 mm x 1303.0 mm. 1500 V. | Unit | 46048
1.2 | Structure
1.2.1 | Horizontal single axis tracker: Generic (default) - Generic tracker (1V) (1 strings) | Unit | 1439
1.3 | Inverter
1.3.1 | ABB - PVS980-58-1909kVA-J (2100 kVA) | Unit | 11
1.4 | Power Station
1.4.1 | Power Station up to 2100 kVA - 630 V/20 kV, with a Two-winding transformer (Dyn11) of 2100 kVA. | Unit | 11
2 | CIVIL WORKS
2.1 | Site Conditions
2.1.1 | Clearing and grubbing | m2 | 683663.51
2.1.2 | Topsoil and vegetacion removal | m3 | 136732.7
2.1.3 | Internal roads (4.0 m width) | m | 7009.28
2.1.4 | Road ditches (Optional) | m | 7009.28
2.2 | Earth works
2.2.1 | Total earth works fill volume | m3 | 21041.91
2.2.2 | Total earth works cut volume | m3 | 19687.68
2.3 | Foundations
2.3.1 | Power Station foundation | Unit | 11
2.3.2 | Structure Poles | Unit | 11512
2.4 | Trenches and manholes
2.4.1 | Low Voltage trenches 400.0 mm x 1000.0 mm | m3 | 3464.37
|  | m | 8660.93
2.4.2 | Low Voltage manholes | Unit | 195
2.4.3 | Medium Voltage trenches 800.0 mm x 1000.0 mm | m3 | 1999.75
|  | m | 2499.68
2.4.4 | Medium Voltage trenches 800.0 mm x 1500.0 mm | m3 | 1039.7
|  | m | 866.42
2.4.5 | Medium Voltage manholes | Unit | 78
2.4.6 | Earthing trenches | m3 | 82.32
2.4.7 | Ancillary services trenches | m3 | 489.59
2.5 | Security and control
2.5.1 | Chain link fence | m | 3263.96
2.5.2 | Access gate | Unit | 1
2.5.3 | Light pole foundation | Unit | 66
2.5.4 | Videocamera foundation | Unit | 33
3 | ELECTRICAL SYSTEM
3.1 | LV DC Electrical cabling (Strings to string box)
3.1.1 | DC cable XLPE Cu 1x(1x10 mm2) | m | 64428.65
3.1.2 | DC cable XLPE Cu 1x(1x4 mm2) | m | 17315.25
3.2 | LV DC Electrical cabling (String box to Inv.)
3.2.1 | DC cable XLPE Al 1x(1x300 mm2) | m | 22148.07
3.2.2 | DC cable XLPE Al 1x(1x630 mm2) | m | 6277.65
3.3 | MV Electrical cabling (From Power Station to Substation)
3.3.1 | MV cable XLPE Al 1x(1x150 mm2) | m | 18792.64
3.3.2 | MV cable XLPE Al 1x(1x240 mm2) | m | 6602.55
3.4 | DC Electrical Box
3.4.1 | DC Electrical Box (13 inputs) | Unit | 101
3.4.2 | DC Electrical Box (6 inputs) | Unit | 9
3.4.3 | DC Electrical Box (8 inputs) | Unit | 9
3.5 | Earthing System
3.5.1 | Earthing cable 35 mm2 (LV & MV trenches) | m | 12027.03
3.5.2 | Earthing cable 50 mm2 (Power Station) | m | 365.86
3.5.3 | Earthing rods (Power Station) | Unit | 88
3.6 | AC Ancillary System
3.6.1 | Auxiliary AC Cable for the perimeter (XLPE 0.6/1 kV Al 4x6 mm2) | m | 3263.96
3.7 | Communication / Monitoring System
3.7.1 | Multimode Fiber Optic Cable (Control System) | m | 8465.06
3.7.2 | Single Mode Fiber Optic Cable (Security System) | m | 3263.96
3.7.3 | RS 485 Com cable (Monitoring System) | m | 11026.86
3.8 | Connectors
3.8.1 | DC male and female connectors | Unit | 2878
3.8.2 | MV Connectors | Unit | 60
4 | MISCELLANEOUS
4.1 | Monitoring system
4.1.1 | Weather Station | Unit | 2
4.1.2 | Monitoring system (SCADA) | Unit | 1
4.1.3 | Remote Terminal Units | Unit | 11
4.2 | Security and Control System
4.2.1 | Control Unit | Unit | 1
4.2.2 | Lighting | Unit | 66
4.2.3 | Video cameras | Unit | 33
4.2.4 | Domo cameras | Unit | 2
4.2.5 | Microwave barriers | Unit | 66
4.2.6 | Microphone cable (perimeter fence) | m | 3263.96
4.3 | Buildings
4.3.1 | Control Room Building | Unit | 1
4.3.2 | Warehouse Building | Unit | 1

## LINE TO TRANSFORMER BoQ
Project | Webinar- Topography
Design | Webinar- Topography-0 | Date | 2024/02/15
Item |  | Unit | Quantity
1 | POWER TRANSFORMER SYSTEM
1.1 | Power Transformer | Total | 1
1.1.1 | Two-winding power transformer (Ydn11) - 220.0 kV/20.0 kV, 25.0 MVA | Unit | 1
1.2 | HV winding earthing | Total | 1
1.2.1 | Primary winding neutral earthing | Unit | 1
1.3 | MV winding earthing | Total | 1
1.3.1 | Reactance - 4.62Ω, 800 A | Unit | 1
1.3.2 | Resistance - 14.43Ω | Unit | 1
1.3.3 | Current Transformer - 24.0 kV, 1000.0 A/5.0 A | Unit | 1
1.3.4 | Disconnector - 24.0 kV, 1250.0 A, 25.0 kA | Unit | 1
1.4 | MV surge arrester | Total | 1
1.4.1 | Surge arrester - Ur:21.0 kV, 10 kA | Unit | 1
1.5 | MV cable
1.5.1 | MV cable length | m | 119.28
2 | HV SYSTEM EQUIPMENT
2.1 | Output Circuit Bay | Total | 1
2.1.1 | Surge arrester - Ur:210.0 kV, 10 kA | Unit | 2
2.1.2 | Earthing disconnector - 245.0 kV, 2000.0 A, 50.0 kA | Unit | 1
2.1.3 | Current Transformer - 245.0 kV, 100.0 A/5.0 A-5.0 A-5.0 A | Unit | 1
2.1.4 | Voltage Transformer - 220.0 kV | Unit | 1
2.1.5 | Circuit breaker - 245.0 kV, 2000.0 A, 50.0 kA | Unit | 1
3 | MV SYSTEM EQUIPMENT
3.1 | Input feeder MV cubicle | Total | 2
3.1.1 | Circuit breaker - 24.0 kV, 630.0 A, 25.0 kA | Unit | 2
3.1.2 | Earthing disconnector - 24.0 kV, 630.0 A, 25.0 kA | Unit | 2
3.1.3 | Current Transformer - 24.0 kV, 600.0 A/5.0 A | Unit | 2
3.2 | Output feeder MV cubicle | Total | 1
3.2.1 | Circuit breaker - 24.0 kV, 1250.0 A, 25.0 kA | Unit | 1
3.2.2 | Earthing disconnector - 24.0 kV, 1250.0 A, 25.0 kA | Unit | 1
3.2.3 | Current Transformer - 24.0 kV, 1000.0 A/5.0 A | Unit | 1
3.3 | Metering MV cubicle | Total | 1
3.3.1 | Earthing disconnector - 24.0 kV, 630.0 A, 25.0 kA | Unit | 1
3.3.2 | Voltage Transformer - 20.0 kV | Unit | 1
3.4 | Auxiliary MV cubicle | Total | 1
3.4.1 | Earthing disconnector - 24.0 kV, 630.0 A, 25.0 kA | Unit | 1
3.4.2 | Fuse - 10.0 A | Unit | 1
3.4.3 | Auxiliary power transformer - 100.0 kW | Unit | 1
4 | CIVIL WORKS
4.1 | Site Conditions
4.1.1 | Clearing and grubbing | m2 | 1866.13
4.1.2 | Topsoil and vegetacion removal | m3 | 373.23
4.1.3 | Internal roads (4.0 m width) | m | 77.78
4.1.4 | Road ditches (Optional) | m | 77.78
4.2 | Buildings
4.2.1 | Control Room Building | m2 | 150
4.3 | Security and control
4.3.1 | Chain link fence | m | 186.36
4.3.2 | Access gate | Unit | 2
4.3.3 | Videocamera foundation | Unit | 1
4.3.4 | Light pole foundation | Unit | 3
5 | MISCELLANEOUS
5.1 | Monitoring system
5.1.1 | Monitoring system (SCADA) | Unit | 1
5.2 | Security and Control System
5.2.1 | Control Room Building | Unit | 1
5.2.2 | Fire system | Unit | 1
5.2.3 | Surveillance system | Unit | 1
5.2.4 | Lightning system | Unit | 3